## Gauge PSI
Directions:
Only fill out the (3) shaded boxes and then copy and paste to your drawing.
Note: This calculation does NOT work for systems supplied by pumps (i.e., LVVWD systems).
APPROXIMATE MINIMUM STATIC PRESSURE @ GAUGE (BASED ON A GAUGE ELEVATION OF 5 FEET A.F.F)
Fire Hydrant Elevation | 2200 | Static Pressure | 70
Finished Floor Elevation | 2250 | Pressure Difference | -23.8315
Elevation Difference at "Gauge" | -55 | Static Pressure at Gauge | 46