## Instructions
1) | Fill out the "Development" information for the top of "Cover Sheet" tab |  | 4) | For each 'Plan or Model' you will take the worst case calculation data and fill in the colored boxes (as shown within the clouded regions).
2) | Fill out the information* for each lot on the "Cover Sheet" tab
This will fill out the table and auto populate all of the white cells to determine the safety margins for each lot with this design.
*Note: only colored (shaded) boxes need information.
3) | Along the bottom you will see just one tab for the 1st model plan info.
If you need more you can just copy one of the plan tabs over and it will retain the link to the cover sheet.
Based on the values entered on cover sheet (Tab) and each plan (type) the highest lot and lowest lots change colors. Additionally the lowest 5 safety margins also change colors.
The calculation will also provide notificaiton through red colored shading if you do not have a 10 psi safety margin.
5) | The "Cover Sheet" table needs to be on the cover sheet of
your Sprinkler Standard Plans. Showing every lot
| in the designed development. |  | If you have less than 100 lots in your development I would delete the extra cells not needed.
Note:
1) This table is limited to 100 Lots if your development has more than 100 create an additional table.
2) The data you fill in here auto fills in on the "Plan ?" tabs. This will prevent multiple data entries, etc…
You will then need to delete the coresponding cells in the "Plan A" tab
Once you have deleted the cells from "Plan A" tab you can then copy the tab over to create the other Model plan info.

## Cover Sheet
Development
Pressure Zone |  | 1780 | Highest Lot Elev. | 1604.9
Fire Hyd. Elev. |  | 1598 | Lowest Lot Elev. | 1597.7
F.H. Static |  | 75
Lot # | F.F. Elev. |  | Approximate Supply to MTR length | Approximate MTR to House length
1 | 1600.9 |  | 21.125 | 12.167
2 | 1600.9 |  | 21.125 | 12.167
3 | 1600.9 |  | 21.125 | 12.167
4 | 1604.9 |  | 21.25 | 24
5 | 1600.6 |  | 7.625 | 11
6 | 1600.6 |  | 7.625 | 11
7 | 1600.6 |  | 7.625 | 11
8 | 1600.6 |  | 7.625 | 11
9 | 1600 |  | 7.625 | 24
10 | 1600 |  | 7.625 | 24
11 | 1600 |  | 7.625 | 24
12 | 1600 |  | 7.625 | 24
13 | 1600 |  | 7.625 | 24
14 | 1598.1 |  | 10.083 | 16.375
15 | 1598.1 |  | 10.083 | 16.375
16 | 1598.1 |  | 10.083 | 16.375
17 | 1598.1 |  | 10.083 | 16.375
18 | 1598.1 |  | 10.083 | 16.375
19 | 1598.1 |  | 10.083 | 16.375
20 | 1598.9 |  | 20.583 | 9
21 | 1598.9 |  | 20.583 | 9
22 | 1598.9 |  | 20.583 | 9
23 | 1598.9 |  | 20.583 | 9
24 | 1598.9 |  | 20.583 | 9
25 | 1599.3 |  | 20.583 | 9
26 | 1598.9 |  | 20.583 | 9
27 | 1598.9 |  | 20.583 | 9
28 | 1599.9 |  | 20.792 | 8
29 | 1599.9 |  | 20.792 | 8
30 | 1599.9 |  | 20.792 | 8
31 | 1599.9 |  | 20.792 | 8
32 | 1600.6 |  | 20.792 | 8
33 | 1600.6 |  | 20.792 | 8
34 | 1600.6 |  | 20.792 | 8
35 | 1600.6 |  | 20.792 | 8
36 | 1598.3 |  | 20.292 | 8
37 | 1598.3 |  | 20.292 | 8
38 | 1598.3 |  | 20.292 | 8
39 | 1598.3 |  | 20.292 | 8
40 | 1597.7 |  | 18.042 | 8
41 | 1597.7 |  | 18.042 | 8
42 | 1597.7 |  | 18.042 | 8
43 | 1597.7 |  | 18.042 | 8
44 | 1597.7 |  | 18.042 | 8
45 | 1597.7 |  | 18.042 | 8
46 | 1597.7 |  | 18.042 | 8
47 | 1597.7 |  | 18.042 | 8
48 | 1597.7 |  | 18.042 | 8
49 | 1597.7 |  | 18.042 | 8
50 | 1597.7 |  | 18.042 | 8
51 | 1597.7 |  | 18.042 | 8
52 | 1597.7 |  | 18.042 | 8
53 | 1597.7 |  | 18.042 | 8
54 | 1597.7 |  | 18.042 | 8
55 | 1597.7 |  | 18.042 | 8
56 | 1597.7 |  | 18.042 | 8
57 | 1597.7 |  | 18.042 | 8
58 | 1597.7 |  | 18.042 | 8
59 | 1597.7 |  | 18.042 | 8
60 | 1597.7 |  | 18.042 | 8
61 | 1597.7 |  | 18.042 | 8
62 | 1597.7 |  | 18.042 | 8
63 | 1597.7 |  | 18.042 | 8
64 | 1597.7 |  | 18.042 | 8
65 | 1597.7 |  | 18.042 | 8
66 | 1597.7 |  | 18.042 | 8
67 | 1597.7 |  | 18.042 | 8
68 | 1597.7 |  | 18.042 | 8
69 | 1597.7 |  | 18.042 | 8
70 | 1597.7 |  | 18.042 | 8
71 | 1597.7 |  | 18.042 | 8
72 | 1597.7 |  | 18.042 | 8
73 | 1597.7 |  | 18.042 | 8
74 | 1597.7 |  | 18.042 | 8
75 | 1597.7 |  | 18.042 | 8
76 | 1597.7 |  | 18.042 | 8
77 | 1597.7 |  | 18.042 | 8
78 | 1597.7 |  | 18.042 | 8
79 | 1597.7 |  | 18.042 | 8
80 | 1597.7 |  | 18.042 | 8
81 | 1597.7 |  | 18.042 | 8
82 | 1597.7 |  | 18.042 | 8
83 | 1597.7 |  | 18.042 | 8
84 | 1597.7 |  | 18.042 | 8
85 | 1597.7 |  | 18.042 | 8
86 | 1597.7 |  | 18.042 | 8
87 | 1597.7 |  | 18.042 | 8
88 | 1597.7 |  | 18.042 | 8
89 | 1597.7 |  | 18.042 | 8
90 | 1597.7 |  | 18.042 | 8
91 | 1597.7 |  | 18.042 | 8
92 | 1597.7 |  | 18.042 | 8
93 | 1597.7 |  | 18.042 | 8
94 | 1597.7 |  | 18.042 | 8
95 | 1597.7 |  | 18.042 | 8
96 | 1597.7 |  | 18.042 | 8
97 | 1597.7 |  | 18.042 | 8
98 | 1597.7 |  | 18.042 | 8
99 | 1597.7 |  | 18.042 | 8
100 | 1591.3 |  | 10.083 | 7

## Plan A
Development |  |  |  |  | Plan Type A |  |  |  | These columns to be on the sprinkler plan at a minimum! (If you cannot fit all on each model sheet)
Pressure Zone |  | 1780 | To MTR Calc Lgth | Supply to MTR Calc Loss | Worst Case Safety Margin(from calc) | 24.5 | <-- Worst Case Safety from your lot calculation |  |  |  | These Columns not needed on the plans
|  |  | 24 | 0.251
Fire Hyd. Elev. |  | 1598 | MTR to House Lngth | MTR to House Calc Loss | Highest Lot Elev. | 1604.9 | Worst Case Safety by lot (In Spreadsheet) | 21.539 | Development
Static |  | 75 | 20.5 | 0.189 | Lowest Lot Elev. | 1597.7 |  |  |  |  | Fill In Yellow Boxes
Lot # | F.F. Elev. | Elevation Difference (From Hydrant) | Elevation Pressure Gain / Loss | Approximate Supply to MTR length | Supply to MTR PSI ADJ | Approximate MTR to House length | MTR to House PSI ADJ | ADJ Safety Margin | Min Static Guage Pres. +/- for 10 PSI | Lot # | Pressure Difference (From Static) | Static @Guage (+5')
1 | 1600.9 | 2.9 | -1.2566 | 21.125 | 0.72162 | 12.167 | 1.5749 | 25.54 | 56.0369 | 1 | -1.2566 | 71.5769
2 | 1600.9 | 2.9 | -1.2566 | 21.125 | 0.72162 | 12.167 | 1.5749 | 25.54 | 56.0369 | 2 | -1.2566 | 71.5769
3 | 1600.9 | 2.9 | -1.2566 | 21.125 | 0.72162 | 12.167 | 1.5749 | 25.54 | 56.0369 | 3 | -1.2566 | 71.5769
4 | 1604.9 | 6.9 | -2.9898 | 21.25 | 0.69025 | 24 | -0.6615 | 21.539 | 58.3048 | 4 | -2.9898 | 69.8437
5 | 1600.6 | 2.6 | -1.1266 | 7.625 | 4.1101 | 11 | 1.7955 | 29.279 | 52.4279 | 5 | -1.1266 | 71.7069
6 | 1600.6 | 2.6 | -1.1266 | 7.625 | 4.1101 | 11 | 1.7955 | 29.279 | 52.4279 | 6 | -1.1266 | 71.7069
7 | 1600.6 | 2.6 | -1.1266 | 7.625 | 4.1101 | 11 | 1.7955 | 29.279 | 52.4279 | 7 | -1.1266 | 71.7069
8 | 1600.6 | 2.6 | -1.1266 | 7.625 | 4.1101 | 11 | 1.7955 | 29.279 | 52.4279 | 8 | -1.1266 | 71.7069
9 | 1600 | 2 | -0.8666 | 7.625 | 4.1101 | 24 | -0.6615 | 27.082 | 54.8849 | 9 | -0.8666 | 71.9669
10 | 1600 | 2 | -0.8666 | 7.625 | 4.1101 | 24 | -0.6615 | 27.082 | 54.8849 | 10 | -0.8666 | 71.9669
11 | 1600 | 2 | -0.8666 | 7.625 | 4.1101 | 24 | -0.6615 | 27.082 | 54.8849 | 11 | -0.8666 | 71.9669
12 | 1600 | 2 | -0.8666 | 7.625 | 4.1101 | 24 | -0.6615 | 27.082 | 54.8849 | 12 | -0.8666 | 71.9669
13 | 1600 | 2 | -0.8666 | 7.625 | 4.1101 | 24 | -0.6615 | 27.082 | 54.8849 | 13 | -0.8666 | 71.9669
14 | 1598.1 | 0.1 | -0.04333 | 10.083 | 3.4932 | 16.375 | 0.77963 | 28.7295 | 54.0607 | 14 | -0.04333 | 72.7902
15 | 1598.1 | 0.1 | -0.04333 | 10.083 | 3.4932 | 16.375 | 0.77963 | 28.7295 | 54.0607 | 15 | -0.04333 | 72.7902
16 | 1598.1 | 0.1 | -0.04333 | 10.083 | 3.4932 | 16.375 | 0.77963 | 28.7295 | 54.0607 | 16 | -0.04333 | 72.7902
17 | 1598.1 | 0.1 | -0.04333 | 10.083 | 3.4932 | 16.375 | 0.77963 | 28.7295 | 54.0607 | 17 | -0.04333 | 72.7902
18 | 1598.1 | 0.1 | -0.04333 | 10.083 | 3.4932 | 16.375 | 0.77963 | 28.7295 | 54.0607 | 18 | -0.04333 | 72.7902
19 | 1598.1 | 0.1 | -0.04333 | 10.083 | 3.4932 | 16.375 | 0.77963 | 28.7295 | 54.0607 | 19 | -0.04333 | 72.7902
20 | 1598.9 | 0.9 | -0.38997 | 20.583 | 0.85767 | 9 | 2.1735 | 27.1412 | 55.3023 | 20 | -0.38997 | 72.4435
21 | 1598.9 | 0.9 | -0.38997 | 20.583 | 0.85767 | 9 | 2.1735 | 27.1412 | 55.3023 | 21 | -0.38997 | 72.4435
22 | 1598.9 | 0.9 | -0.38997 | 20.583 | 0.85767 | 9 | 2.1735 | 27.1412 | 55.3023 | 22 | -0.38997 | 72.4435
23 | 1598.9 | 0.9 | -0.38997 | 20.583 | 0.85767 | 9 | 2.1735 | 27.1412 | 55.3023 | 23 | -0.38997 | 72.4435
24 | 1598.9 | 0.9 | -0.38997 | 20.583 | 0.85767 | 9 | 2.1735 | 27.1412 | 55.3023 | 24 | -0.38997 | 72.4435
25 | 1599.3 | 1.3 | -0.56329 | 20.583 | 0.85767 | 9 | 2.1735 | 26.9679 | 55.3023 | 25 | -0.56329 | 72.2702
26 | 1598.9 | 0.9 | -0.38997 | 20.583 | 0.85767 | 9 | 2.1735 | 27.1412 | 55.3023 | 26 | -0.38997 | 72.4435
27 | 1598.9 | 0.9 | -0.38997 | 20.583 | 0.85767 | 9 | 2.1735 | 27.1412 | 55.3023 | 27 | -0.38997 | 72.4435
28 | 1599.9 | 1.9 | -0.82327 | 20.792 | 0.80521 | 8 | 2.3625 | 26.8444 | 55.1658 | 28 | -0.82327 | 72.0102
29 | 1599.9 | 1.9 | -0.82327 | 20.792 | 0.80521 | 8 | 2.3625 | 26.8444 | 55.1658 | 29 | -0.82327 | 72.0102
30 | 1599.9 | 1.9 | -0.82327 | 20.792 | 0.80521 | 8 | 2.3625 | 26.8444 | 55.1658 | 30 | -0.82327 | 72.0102
31 | 1599.9 | 1.9 | -0.82327 | 20.792 | 0.80521 | 8 | 2.3625 | 26.8444 | 55.1658 | 31 | -0.82327 | 72.0102
32 | 1600.6 | 2.6 | -1.1266 | 20.792 | 0.80521 | 8 | 2.3625 | 26.5411 | 55.1658 | 32 | -1.1266 | 71.7069
33 | 1600.6 | 2.6 | -1.1266 | 20.792 | 0.80521 | 8 | 2.3625 | 26.5411 | 55.1658 | 33 | -1.1266 | 71.7069
34 | 1600.6 | 2.6 | -1.1266 | 20.792 | 0.80521 | 8 | 2.3625 | 26.5411 | 55.1658 | 34 | -1.1266 | 71.7069
35 | 1600.6 | 2.6 | -1.1266 | 20.792 | 0.80521 | 8 | 2.3625 | 26.5411 | 55.1658 | 35 | -1.1266 | 71.7069
36 | 1598.3 | 0.3 | -0.12999 | 20.292 | 0.93071 | 8 | 2.3625 | 27.6632 | 55.0403 | 36 | -0.12999 | 72.7035
37 | 1598.3 | 0.3 | -0.12999 | 20.292 | 0.93071 | 8 | 2.3625 | 27.6632 | 55.0403 | 37 | -0.12999 | 72.7035
38 | 1598.3 | 0.3 | -0.12999 | 20.292 | 0.93071 | 8 | 2.3625 | 27.6632 | 55.0403 | 38 | -0.12999 | 72.7035
39 | 1598.3 | 0.3 | -0.12999 | 20.292 | 0.93071 | 8 | 2.3625 | 27.6632 | 55.0403 | 39 | -0.12999 | 72.7035
40 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 40 | 0.12999 | 72.9635
41 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 41 | 0.12999 | 72.9635
42 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 42 | 0.12999 | 72.9635
43 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 43 | 0.12999 | 72.9635
44 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 44 | 0.12999 | 72.9635
45 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 45 | 0.12999 | 72.9635
46 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 46 | 0.12999 | 72.9635
47 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 47 | 0.12999 | 72.9635
48 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 48 | 0.12999 | 72.9635
49 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 49 | 0.12999 | 72.9635
50 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 50 | 0.12999 | 72.9635
51 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 51 | 0.12999 | 72.9635
52 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 52 | 0.12999 | 72.9635
53 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 53 | 0.12999 | 72.9635
54 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 54 | 0.12999 | 72.9635
55 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 55 | 0.12999 | 72.9635
56 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 56 | 0.12999 | 72.9635
57 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 57 | 0.12999 | 72.9635
58 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 58 | 0.12999 | 72.9635
59 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 59 | 0.12999 | 72.9635
60 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 60 | 0.12999 | 72.9635
61 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 61 | 0.12999 | 72.9635
62 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 62 | 0.12999 | 72.9635
63 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 63 | 0.12999 | 72.9635
64 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 64 | 0.12999 | 72.9635
65 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 65 | 0.12999 | 72.9635
66 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 66 | 0.12999 | 72.9635
67 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 67 | 0.12999 | 72.9635
68 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 68 | 0.12999 | 72.9635
69 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 69 | 0.12999 | 72.9635
70 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 70 | 0.12999 | 72.9635
71 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 71 | 0.12999 | 72.9635
72 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 72 | 0.12999 | 72.9635
73 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 73 | 0.12999 | 72.9635
74 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 74 | 0.12999 | 72.9635
75 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 75 | 0.12999 | 72.9635
76 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 76 | 0.12999 | 72.9635
77 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 77 | 0.12999 | 72.9635
78 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 78 | 0.12999 | 72.9635
79 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 79 | 0.12999 | 72.9635
80 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 80 | 0.12999 | 72.9635
81 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 81 | 0.12999 | 72.9635
82 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 82 | 0.12999 | 72.9635
83 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 83 | 0.12999 | 72.9635
84 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 84 | 0.12999 | 72.9635
85 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 85 | 0.12999 | 72.9635
86 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 86 | 0.12999 | 72.9635
87 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 87 | 0.12999 | 72.9635
88 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 88 | 0.12999 | 72.9635
89 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 89 | 0.12999 | 72.9635
90 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 90 | 0.12999 | 72.9635
91 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 91 | 0.12999 | 72.9635
92 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 92 | 0.12999 | 72.9635
93 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 93 | 0.12999 | 72.9635
94 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 94 | 0.12999 | 72.9635
95 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 95 | 0.12999 | 72.9635
96 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 96 | 0.12999 | 72.9635
97 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 97 | 0.12999 | 72.9635
98 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 98 | 0.12999 | 72.9635
99 | 1597.7 | -0.3 | 0.12999 | 18.042 | 1.4955 | 8 | 2.3625 | 28.4879 | 54.4755 | 99 | 0.12999 | 72.9635
100 | 1591.3 | -6.7 | 2.9031 | 10.083 | 3.4932 | 7 | 2.5515 | 33.4478 | 52.2888 | 100 | 2.9031 | 75.7366